## Slide 1: Load Flow Analysis
Summer Internship Seminar
By:
Siddharth Bhal
Electrical Eng. Dept.
IIT Roorkee.
19th May to 4th July, 2011

## Slide 2: Outline
Introduction to RIL, Patalganga
Power system
Load flow
Motor Analysis
Conclusion

## Slide 3: Introduction to RIL, Patalganga

## Slide 4: RIL
Largest private sector company in India.
Annual revenues ~ US$ 58.5 billion.
126th position in Fortune Global 2000 list.
Core business: petrochemicals and textiles.
Mother plant.
Backward Vertical integration
Complex power system
RIL, Patalganga
Notes: Major subsidiaries
Reliance Life Sciences
Reliance Industrial Infrastructure Limited
Reliance Solar

## Slide 5
Products manufactured | Raw materials
Para Xylene (Px) | Naphtha
Purified Terephthalic Acid (PTA) | Para Xylene
Polyester Filament Yarn (PFY) | PTA & MEG
Polyester Staple Fibre (PSF) | PTA & MEG
Linear Alkyl Benzene (LAB) | Kerosene & paraffin
Name of Plant | Commissioned Year
Polyester Filament Yarn (PFY) | Oct.1982
Polyester Staple Fiber (PSF) | Mar.1986
Purified Terephthalic Acid (PTA) | Feb.1988
Paraxylene Plant (PX) | Nov.1988
Linear Alkyl Benzene Plant (LAB) | Nov. 1987
L A B (Front End) | Mar.1992

## Slide 6: Power System

## Slide 9: Load Flow Analysis
Using ETAP

## Slide 10: Assumptions
Grid Fault Level
Generators Output
Motor power factors
Lumped loads
ENC load equally divided
Cable lengths
Initial voltage
DG sets excluded
Notes: 80% constant KVA loads (motors) and
20% constant impedence loads

## Slide 11: Schema 1
Fibre load: | 31.6 MW. | STG output: | 8 MW @ 79% pf
ENC load: | 19.6 MW | Zig-Zag Tranf. | Off
GTG1 output: | 27 MW @ 88% pf. | LA,LB: | On
GTG2 output: | 27 MW @ 84% pf | MSEB Grid | Charged
DG’s | Off | TA-1 | On
TA-2 | On | TA-3 | On

## Slide 14: Motor startup analysis

## Slide 15: LLP-J Motor Specifications
Frame size: | 8012 | Rated Output: | 2125 KW
Voltage Level: | 11 Kv | Service factor: | 1
Operating Freq | 50 Hz. | Rated Speed | 2977 rpm
Efficiency(1/2 load) | 94.4 | Full Load Ampere | 127 amp
Efficiency(3/4 load) | 95.0 | Locked Rotor Ampere | 742 amp
Efficiency(full load) | 94.9 | No Load Ampere | 17.1 amp
PF (1/2 Load) | 91.5 | Full load torque | 5028 lb-ft
PF (3/4 Load) | 92.8 | Starting Torque | 3268 lb-ft
PF (Full Load) | 92.5 | Breakdown Torque | 11313 lb-ft
Rotor wk2 | 1244 lbs-ft2 | Motor Weight | 26700 lbs
Customer wk2 | 1602 lbs-ft2 | Rotor Weight | 4014 lbs

## Slide 16
Motor Terminal Voltage (% of motor rated volt) vs Time (sec)
Motor Current (amp) vs Time (sec)

## Slide 17
Motor Torque vs Time(sec)
Motor Slip vs Time(sec)

## Slide 18: Conclusion
Industrial application of electrical machines
Working Principles in Large Scale Industries
ETAP
Professional life of the engineers
Safety standards and Maintenance practices

## Slide 19
Thank you!